| CONFIRMATION OF VERIFICATION EVIDENCE REPORT [All generators greater than 10kW, shall be complete and submit this report before energization] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Section 1 |  |  |  | BASIC INFORMATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Name of Customer |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Name of Facility |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Address |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Generator Capacity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Station & Feeder |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Type of Generation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Section 2 |  |  |  | SIGNATURES / CERTIFICATES |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TO BE SIGNED UPON COMPLETION OF ALL PARTS OF THE COVER I/we acknowledge the completion of the COVER as noted and will undertake to rectify the deficiencies identified in the “NOTES” section. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | I certify that the attached results/reports were undertaken/reviewed by the undersigned and are in conformance with all requirements, except as noted herein. |  |  |  |  |  |  |  |  |  |
| Signature of Customer Representative |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Print Name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: |  |  |  |  |  |  |  |  | Signature of Engineer Certifying report |  |  |  |  |  |  |  |  |  |
| Title/Affiliation: |  |  |  |  |  |  |  |  | Print Name: |  |  |  |  | P.Eng |  |  |  |  |
| Email: |  |  |  |  |  |  |  |  | Date: |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Title/Affiliation: |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Email: |  |  |  |  |  |  |  |  |  |
| Section 3 |  |  |  | DISTRIBUTION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Distribution List (when all parts are completed): |  |  |  |  |  |  |  | ENWIN Coordinator: |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Print Name: |  |  |  |  |  |  |  |  |  |  |
|  | Transmitter (Customer Business Relations), |  |  |  |  |  |  | Title: |  |  |  |  |  |  |  |  |  |  |
|  | ENWIN System Planning/Engineering |  |  |  |  |  |  | Date: |  |  |  |  |  |  |  |  |  |  |
|  | Customer, |  |  |  |  |  |  | Tel: |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Email: |  |  |  |  |  |  |  |  |  |  |
| Section 4(a) |  |  |  | CONFIRMATION OF VERIFICATION – PROTECTION & CONTROL |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Complete for Load Displacement / Export generators connected at 27.6kV Confirm the following Protection & Control requirements are in place and operating properly |  |  |  |  |  |  |  |  |  | Protection Group |  | Legend | Results |  |  | Note # | Initials | Date yyyy/mm/dd |
| - LV Bus Main and Backup Unit Protection Scheme |  |  |  |  |  |  |  |  |  | C |  |  |  |  |  |  |  |  |
| - Transformer Main and Backup Protection Scheme |  |  |  |  |  |  |  |  |  | C |  |  |  |  |  |  |  |  |
| - HV Breaker Failure Protection |  |  |  |  |  |  |  |  |  | C |  |  |  |  |  |  |  |  |
| - LV Breaker Failure Protection |  |  |  |  |  |  |  |  |  | C |  |  |  |  |  |  |  |  |
| - Under and Over Frequency |  |  |  |  |  |  |  |  |  | C |  |  |  |  |  |  |  |  |
| - Transfer Trip / Remote Trip |  |  |  |  |  |  |  |  |  | C |  |  |  |  |  |  |  |  |
| - DGEO Test (Generator End Open) |  |  |  |  |  |  |  |  |  | C |  |  |  |  |  |  |  |  |
| - Passive Anti-Islanding Protection (check that the generator disconnects upon loss of utility supply by 0.3s) |  |  |  |  |  |  |  |  |  | C |  |  |  |  |  |  |  |  |
| - Reverse Power (load displacement) |  |  |  |  |  |  |  |  |  | C |  |  |  |  |  |  |  |  |
| - Confirm the installation complies with submitted Single Line Diagram |  |  |  |  |  |  |  |  |  | C |  |  |  |  |  |  |  |  |
| - Other (Specify) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Protection Group to be tested:  e.g. A, B, or A&B, D = to be Done

Legend: C = Confirm, W = Witness

Results: P = Pass, F = Fail

All Parts: N/A = Not Applicable

| Section 4(b) | CONFIRMATION OF VERIFICATION – PROTECTION & CONTROL |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Complete for Load Displacement / Export generators connected at 347/600V or 120/208V Confirm the following Protection & Control requirements are in place and operating properly |  | Protection Group | Legend | Results | Note # | Initials | Date yyyy/mm/dd |
| - Operation of Isolation Switch |  |  |  |  |  |  |  |
| - Synchronous Breaker Failure Protection |  |  |  |  |  |  |  |
| - Transfer Trip / DGEO Test |  |  |  |  |  |  |  |
| - Passive Anti-Islanding Protection (check that the generator disconnects upon loss of utility supply by 0.3s) |  |  |  |  |  |  |  |
| - Under and Over Frequency |  |  |  |  |  |  |  |
| - Under and Over Voltage |  |  |  |  |  |  |  |
| - Reverse Power (load displacement) |  |  |  |  |  |  |  |
| - Confirm the installation complies with submitted Single Line Diagram |  |  |  |  |  |  |  |
| - Other (Specify) |  |  |  |  |  |  |  |

Protection Group to be tested:  e.g. A, B, or A&B, D = to be Done

Legend: C = Confirm, W = Witness

Results: P = Pass, F = Fail

All Parts: N/A = Not Applicable

| Section 4(b1) | CONFIRMATION OF VERIFICATION – PROTECTION & CONTROL |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Complete for Load Displacement / Export generators connected at 120/240V Confirm the following Protection & Control requirements are in place and operating properly |  | Protection Group | Legend | Results | Note # | Initials | Date yyyy/mm/dd |
| - Operation of Isolation Switch |  |  |  |  |  |  |  |
| - Synchronous Breaker Failure Protection |  |  |  |  |  |  |  |
| - Transfer Trip / DGEO Test |  |  |  |  |  |  |  |
| - Passive Anti-Islanding Protection (check that the generator disconnects upon loss of utility supply by 0.3s) |  |  |  |  |  |  |  |
| - Under and Over Frequency |  |  |  |  |  |  |  |
| - Under and Over Voltage |  |  |  |  |  |  |  |
| - Reverse Power (load displacement) |  |  |  |  |  |  |  |
| - Confirm the installation complies with submitted Single Line Diagram |  |  |  |  |  |  |  |
| - Generation limit back to ENWIN grid ( ) |  |  |  |  |  |  |  |
| - Other (Specify) |  |  |  |  |  |  |  |

Protection Group to be tested:  e.g. A, B, or A&B, D = to be Done

Legend: C = Confirm, W = Witness

Results: P = Pass, F = Fail

All Parts: N/A = Not Applicable

| Section 4(c) | CONFIRMATION OF VERIFICATION – PROTECTION & CONTROL |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Complete for Generators connected momentarily to transfer load Confirm the following Protection & Control requirements are in place and operating properly |  | Protection Group | Legend | Results | Note # | Initials | Date yyyy/mm/dd |
| - Operation of Isolation Switch (Confirm the complete transfer is less than 100ms) |  |  |  |  |  |  |  |
| - Confirm the isolation complies with submitted Single Line Diagram |  |  |  |  |  |  |  |
| - Other (Specify) |  |  |  |  |  |  |  |

Protection Group to be tested:  e.g. A, B, or A&B, D = to be Done

Legend: C = Confirm, W = Witness

Results: P = Pass, F = Fail

All Parts: N/A = Not Applicable

| Section 4(d) | CONFIRMATION OF VERIFICATION – PROTECTION & CONTROL |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Complete for Generators not connected momentarily to transfer load Confirm the following Protection & Control requirements are in place and operating properly |  | Protection Group | Legend | Results | Note # | Initials | Date yyyy/mm/dd |
| - Operation of Transfer Switch (Break before Make Functionality) |  |  |  |  |  |  |  |
| - Confirm the isolation complies with submitted Single Line Diagram |  |  |  |  |  |  |  |
| - Other (Specify) |  |  |  |  |  |  |  |

Protection Group to be tested:  e.g. A, B, or A&B, D = to be Done

Legend: C = Confirm, W = Witness

Results: P = Pass, F = Fail

All Parts: N/A = Not Applicable

| Section 5 | CUSTOMER OWNED AND OPERATE DG [not required for generators paralleling utility for less than 100msec] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Confirm the following SCADA telemetry quantities indicate correctly |  | Test Needed | Legend | Results | Note # | Initials | Date yyyy/mm/dd |
| - MW Flows and Directions |  | C |  |  |  |  |  |
| - MVAR Flow and Directions |  | C |  |  |  |  |  |
| - Phase to Phase or Phase to Neutral Voltages |  | C |  |  |  |  |  |
| - Three Phase Currents |  | C |  |  |  |  |  |
| - LV Interrupter Open/Close Status *Hydro One Network Operating Division will specific which status to use |  | C |  |  |  |  |  |
| - Protection Alarms (TT receive from Hydro One and DGEO send) |  | C |  |  |  |  |  |
| - Wireless Link end to end tested |  | C |  |  |  |  |  |
| - Synchronizing Breakers Open/Close Status |  | C |  |  |  |  |  |
| - HV/LV Line Disconnect Switches Open/Close Status |  | C |  |  |  |  |  |
| - Other (Specify) |  |  |  |  |  |  |  |

Test Needed:  D = Done

Legend: C = Confirm, W = Witness

Results: P = Pass, F = Fail

All Parts: N/A = Not Applicable

| Section 6 |  | NOTES |
| --- | --- | --- |

Instructions for Completing the COVER form:

Step 1: Discuss with the ENWIN Coordinator and decide what protection test / controls are required.

Step 2: Complete Intended Tests

Step 3: Send original signed COVER Report to:

Attn: Technical Services

ENWIN Utilities Ltd.

P. O. Box 1652 Stn. “A”

4545, Rhodes Drive,

Windsor, ON,

N9A 5T7